## UNPriced BoQs FOR 20FT COLDROOM
UNPRICED BOQ & Design for a 20 ft Solar-Powered Cold Room in Lughaya, Somaliland
1. Cold room operating conditions
Cold Room No. | Size of cold room (L×W×H) |  |  | Cold room temperature (°C)
1 | 5×2.3×2.3m |  |  | -15℃
2. Equipment parameters
2.1 Equipment parameters
Device Name |  |  | Cold room
Electricity system |  |  | 380V/3PH/50HZ
Refrigerant |  |  | R507/R404a
Condensing way |  |  | Air-cooled condenser
2.2 Cold Room Panel & Door Technical Details
Cold room panel |  | Insulation Material | Polyurethane (PU)
|  | Density | 40±2kg/m³
|  | Thickness | 100mm
|  | Double-layer material (Roof and walls) | 0.326 mm color steel on both sides
|  | Floor | 0.326 mm color steel on both the inside and outside
Cold room door |  | Insulation Material | Polyurethane (PU)
|  | Density | 40±2kg/m³
|  | Thickness | 100mm
|  | Dimension of the door | 800×1800mm
|  | Double-layer material | 0.5 mm color steel on both sides
Auxiliary materials |  | Accessories, pressure balance window & cold room lights | Supplies such as glass sealant, hardware, etc. The pressure balance window is used to balance the internal and external air pressure. The cold room uses special LED lights.
2.3 Performance parameters for the cold room
| Working conditions |  | Condensing temperature | 45℃
|  |  | Evaporative temperature | -7℃
| Compressor |  | Brand | Copeland
|  |  | Model | ZB15KQE (2 HP)
|  |  | Quantity | 1 set
|  |  | Refrigeration capacity per unit | 2.39 kW
|  |  | Input power per unit | 2.03 kW
| Air-cooled condenser technical parameters |  | Quantity of condensers | 1 set
|  |  | Number of fans per condenser | 1 pc
|  |  | Power of each condenser | 0.12 kW
| Side-outlet ceiling air cooler |  | Model | DD-7
|  |  | Quantity of air coolers | 1 set
|  |  | Number of fans per air cooler | 1 pc
|  |  | Power of each air cooler | 0.24 kW
|  |  | Electric defrost power of each air cooler | 2 kW
| Expansion valve |  | Brand | Denmark Danfoss
| Electric control box |  | Main brand | Delixi and LG (South Korea) Microcomputer control
| Dimensions of each outdoor refrigeration unit |  |  | 1020×420×780mm
| Dimensions of each indoor air cooler |  |  | 1310×420×475mm
| Copper pipe |  |  | Liquid supply and gas return pipes, insulation, and cable ties included
| Cable |  |  | Cables for the compressor, fan, cold room light, and temperature controller: 1 set
| Installation accessories |  |  | Cable trays, drainage pipes, etc.: 1 set
2.4 Performance parameters for the solar power system
| Photovoltaic/ solar panels |  | Power | 550 W/pc
|  |  | Quantity | 10 pcs
| Inverter |  | Type | Hybrid
|  |  | Power | 6.2 KW
| Storage battery |  | Calculation | 51.2 V × 314 Ah
|  |  | Energy per unit | 16 kWh/unit
|  |  | Quantity | 1 pc
| Support |  | Photovoltaic panel mounting brackets | 10 pcs
| Other accessories |  | Battery-pack parallel connection cable, battery combiner box, waterproof photovoltaic circuit breaker, waterproof photovoltaic MC4 connector, and complete set of red and black photovoltaic cables: 1 set
ITEMS | DESCRIPTION | UNIT | UNIT PRICE | TOTAL AMOUNT
1 | Supply and install a 20 ft solar-powered freezer room (Copeland 2 HP compressor unit, 100 mm-thick sandwich panels, 5.5 kW solar panels, 6.2 kW inverter, and 16 kWh battery). | 1 |  | 0
GRAND TOTAL |  |  |  | 0
Contact Person:….............................................................................................
Company Name:…………………........................................................................
Address: ………………………………………………………………………………………………
Tel No: …………………………………………………………………………………………………
Date:…………………………………………………………………………………………………….
Signed:….............................................................................................................
Stamp: ...…………………………………………………………………………………...............
3. Pictures Standardized Design & Pictures for Reference
Cold room panels forming the cold room body, properly aligned to receive maximum sunlight; containerized cold room interior.
Outdoor compressor refrigeration unit, solar panels, inverter, and battery.
Solar-Powered Containerized Cold Room